CITY OF SELDOVIA

## PUBLIC WATER SYSTEM

## PWSID NO. 240707

## 2005 CONSUMER CONFIDENCE REPORT

The City of Seldovia is pleased to present to you this year's Annual Consumer Confidence Report, which covers the January-December 2005 period.  This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. As most of you are aware, the City of Seldovia has been actively working on city water and sewer upgrades for a number of years now, and are nearing completion on a design and engineering study for system-wide upgrades.  We continue to strive to optimize our current treatment system, and to maintain and repair leaks in the water distribution system as needed.

Our water source is surface water from the upper water reservoir located in the hills east of the airport. For those of you that don't know where the reservoir is located, a copy of the topographical map is available for review at the City office.

During 2005, the City of Seldovia operated under the Filtration Avoidance program.   This program, allowed by State and federal regulations allows a water system using a surface water source to treat the raw water without filtration if the system can meet very strict standards governing the raw and treated water quality, system design and watershed control.    Last year, on a few occasions, our water quality did not meet the raw and treated water quality standards for turbidity and/or disinfection, and on these occasions we provided public notice.    Minor modifications have been made to the water treatment plant to help us better monitor the water quality and to improve our ability to respond to poor water quality.   Also, to further address this problem, the City of Seldovia intends to install filtration at the water treatment plant within the next couple of years.   Filtration will enhance the water quality by removing more of the organic matter from the water prior to it being disinfected, and will provide a double-barrier system which will increase the removal and inactivation of micro-organisms that may exist in the raw untreated water source.

Water treatment

Currently, treatment takes place at the chlorination building where chlorine is added to treat the raw water for water born pathogens.  The water is then placed in a 550,000 gallon storage tank. The water moves from the storage tank to the distribution lines serving the city.  The treated water is tested daily for turbidity (clarity), chlorine levels, temperature and pH.  In addition, a weekly sample from the raw water is tested for fecal coliform bacteria.  We also sample five sites around town to test for coliform bacteria and to ensure that the treated water is free of bacteria and to verify that we have an adequate chlorine residual in the distribution system.

There is approximately 15,840 feet of water pipe within Seldovia's distribution system. The water distribution system starts at the upper reservoir and is piped to the chlorinating building. Chlorine is added as the water moves to the tank, then to the distribution lines to the city. The water system is controlled by over 55 valves, and there are 49 fire hydrants.

The water system for Seldovia is controlled by the City of Seldovia.  At present we have one certified water operator, Mary Klinger, OIT, and two other operators; Manfred Kirchner, and Steve Kroll. If you have any questions about this report or your water utility, please contact the City of Seldovia at 234-7643. We want our customers to be informed about their water utility. You may also come to the City of Seldovia Council meetings scheduled for the second and fourth Wednesdays of each month. The meetings are held in the Multipurpose Room.

General Information about Water Tests and Contaminants

As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases radioactive material, and/or it can pick up substances resulting from the presence of animals or from human activity.  Therefore, one can reasonably expect their drinking water, including bottled

water, to contain at least small amounts of some contaminants. It is important to remember that the presence of contaminants does not necessarily indicate that water poses a public health risk, and the risk is dependent

on such things as the level of contamination and the length of exposure.

Contaminants that may be present in source water include: Microbial contaminants, such as viruses and bacteria, which may come from septic systems, agricultural livestock operations, and wildlife;  Inorganic contaminants, such as salts and metal, which can be naturally occurring;  Pesticides and herbicides, which may come from a variety of sources such as agriculture, and residential uses; Organic chemical contaminants, including synthetic and volatile chemicals, which are byproducts of industrial processes and septic systems; and/or, Radioactive contaminants, which can be naturally occurring or by the result of oil and gas mining activities.

We have summarized the water quality test results for 2005 in this report.  Consumers may obtain additional information about individual contaminants and potential health effects can be obtained by calling the Environmental Protection Agency's Safe Drinking Water Hotline at (800-426-4791).

Water Quality Test Results

Our water operators routinely monitor for contaminants in your drinking water according to Federal and State laws. The State requires us to monitor for many contaminants on different schedules. The monitoring requirements vary depending on the water source and contaminant. The following table shows the results of our monitoring for the 2005 year or for the last sample collected.  We did not sample our water for Pesticides and Herbicides due to a waiver by the Department of Environmental Conservation.

Table of Detected Contaminants in 2005

In the table below you will find terms and abbreviations you might not be familiar with. To better help you understand these terms, please review the following definitions:

Parts per million (ppm) or Milligrams per liter (mg/l) - one part per million corresponds to one minute in two years or a single penny in $10,000.

Parts per billion (ppb) or Micrograms per liter - one part per billion corresponds to one minute in 2,000 years, or a single penny in $10,000,000.

Action Level - the concentration of a contaminant which, if exceeded, baggers treatment or other requirements which a water system must follow.

Treatment Technique (TT) - A treatment technique is a required process intended to reduce the level of contaminants in drinking water.

Maximum Contaminant Level - The "Maximum Allowed" (MCL) is the highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal - The "Goal"(MCLG) is the level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

Turbidity - Suspended material or cloudiness, measured in NTU'S. Turbidity has no health effects. However, turbidity can interfere with disinfecting and provide a medium for microbial growth. Turbidity may indicate the presence of disease-causing organisms. These organisms include bacteria, viruses, and parasites that can cause symptoms such as nausea, cramps, diarrhea, and associated headaches.

NTU's - Nephelometric Turbidity Unit, units of turbidity indicated by an instrument (nephelometer) that measures refracted light through a water sample.

2005 SUMMARY

| Contaminant | Level Detected | MCLG | MCL or AL* | Likely Source of Contamination |
| --- | --- | --- | --- | --- |
| 1. Turbidity (Treated Water) | Highest 4.0 NTU (+/-) | N/A | 1.49 NTU | Soil Runoff |
| 2. Lead | 19 ppb | 0 ppb | AL = 15 ppb | Corrosion of Household Plumbing |
| 3. Copper | 2585 ppb | 1300 ppb | AL = 1300 ppb | Corrosion of Household Plumbing |
| 4. Nitrate | 1.94 ppm | 10 ppm | 10 ppm | Erosion of Natural Deposits |
| 5. Total Trihalomethanes | 1.72 ppb | N/A | 80 ppb | Chlorination by-product |
| 6. Haloacetic Acid | 0 ppb | N/A | 60 ppb | Chlorination by-product |

* Compliance with the Lead and Copper Rule is based on 90 percent of the results being less than or equal to the action level (AL).  In 2005 five houses were sampled and 2 exceeded the AL for lead, and 3 houses failed the AL for copper.

Elevated Lead and Copper Levels:  Our lead and copper tests, completed in 2005, indicate that some of the homes tested have elevated levels of lead and copper.  Lead and copper are generally found in the water because it leaches from the water plumbing, solder and fixtures.  We will complete a corrosion control study to determine if we can treat the water in a way to make it less corrosive, which ultimately would reduce the lead and copper “at-the-tap”.  This corrosion control study is being completed along with an entire system design review.  When it is determined what type of treatment we will install, further notice will be provided

Health Affects of Lead and Copper:  Infants and young children are typically more vulnerable to lead and copper in drinking water than the general population.  Prolonged exposure to high levels of lead can cause delay in child development.  Also, studies have shown that prolonged exposure to elevated lead or copper over many years may increase the risk of kidney, liver and/or high blood pressure problems.   The level of exposure is based on all avenues of exposure from air, food, water, etc.  However, EPA sets the action levels for these contaminants for water systems so that appropriate treatment can be installed to reduce the risk.  It is possible that lead or copper levels at your home may be higher than at other homes in the community as a result of materials used in your home’s plumbing. If you are concerned about elevated lead or copper levels in your home’s water, you may wish to have your water tested.  Also, to reduce the level of lead and/or copper at the tap, use your cold water tap for cooking and drinking water.  Always flush the tap for 30 seconds to 2 minutes before using the water for drinking and/or cooking purposes. Additional educational materials on lead and copper are available upon request at City office.

Treatment Technique Violations:  As indicated in prior public notice, the water system had a few occasions when either the turbidity was too high, or the chlorine levels were too low.  These are considered treatment technique (TT) violations.   TT violations indicated that the water may not be adequately treated to remove or destroy micro-organisms.  These organisms may include bacteria, viruses, and parasites that can cause symptoms of nausea, cramps diarrhea and associated headaches (although these may be symptoms of other illness also).    People with severely compromised immune systems, infants, and some elderly may be at increased risk when we have TT violations.   These people should seek advice about drinking water from their health care provider.

At this time, our water is meeting the treatment technique requirements, and we strive daily to provide you with the best water our water treatment plant is capable of producing.

We thank you for allowing us to provide you with a safe dependable water source.  In our continuing efforts to maintain a safe and dependable water supply, it may be necessary to make improvements in the water system, such as the installation of corrosion control treatment and filtration.  The costs of such improvements may result in an increase in your current utility rate.  Your understanding in this matter is appreciated.